** NOTE TO SPECIFIER **  This document is subject to copyright protection and is property of Ruskin Company.  Ruskin authorizes the Specifier a limited non-exclusive license to use this document (in whole or in part) for the purpose of preparing written product specifications for the above CSI MasterFormat category.  Ruskin Company is providing the information contained in this document for informational use, and is provided without representation or warranty of any kind as to the user or any other party, including, without limitation, any implied warranty of merchantability, and fitness for particular purpose, application, or non-infringement. To the greatest extent permitted by applicable law, Ruskin Company assumes no liability, and User assumes all liability and risk, for the use or results from the use of this document or the information contained herein, whether modified by the user or not. Any user of this document should consult www.ruskin.com to verify that the information contained herein is the most current representation of the specified product.

SECTION 23 33 00

CONTROL DAMPERS

Display hidden notes to specifier by using “Tools”/”Options”/“View”/”Hidden Text”.

** NOTE TO SPECIFIER **  This section is based on the products of Ruskin Company, which is located at:

3900 Dr. Greaves Road

Kansas City, Missouri 64030

Tel: (816) 761-7476

Fax: (816) 765-8955

Email: ruskin@ruskin.com

Web: http://www.ruskin.com

Ruskin Manufacturing has been the leading manufacturer of dampers and louvers for 50 years. Ruskin has pioneered advanced products for the HVAC Industry and continues to be an industry leader with modern manufacturing equipment, computer-aided design capabilities and an AMCA registered air performance testing laboratory for research and development. All of these are backed by our experienced engineers and professional staff and reflects Ruskin's commitment to high quality product standards.

Ruskin Commercial Control Dampers are designed to provide construction features that meet the needs of the customers, ambient to extreme temperatures, pressures and challenging atmospheres.  Ruskin can provide ultra-low leakage, high temp and pressure relief dampers for process control. When required non-standard materials can be used to meet or exceed project requirements. Post applied coatings and finishes are also to be considered based on system conditions. Control damper – 6 inches (152 mm) deep steel single skin blade CD35.

SECTION 23 33 00, Copyright 2015, Ruskin Company.

PART 1	GENERAL

1.1	SECTION INCLUDES

A.	Galvanized steel control dampers suitable for applications in HVAC systems with velocities to 2000 feet per minute (610 m/min).

1.2	RELATED SECTIONS

** NOTE TO SPECIFIER **  Edit the following list as required for the project.  List other sections with work directly related to the dampers.

A.	Section 23 31 00 – HVAC Ducts and Casings.

B.	Section 23 09 00 – Instrumentation and Control for HVAC

1.3	REFERENCES

- AMCA 500 - Test Methods for Louvers, Dampers and Shutters.

- AMCA 511 – Certified Ratings Program for Air Control Devices

** NOTE TO SPECIFIER **  Delete if not required.

- USGBC: U.S. Green Building Council LEED® Rating System.

1.4	DEFINITIONS

** NOTE TO SPECIFIER **  Retain definitions remaining after this Section has been edited.

Damper Terminology:  Definitions of terms for metal louvers contained in AMCA 500 apply to this Section unless otherwise defined in this Section or in referenced standards.

Horizontal Damper:  Damper with horizontal blades, i.e., the axes of the blades is horizontal.

Vertical Damper:  Damper with vertical blades, i.e., the axes of the blades is vertical.

1.5	ACTION SUBMITTALS

- Comply with requirements of Section 01 33 00 – Submittal Procedures.

- Product Data:  Submit manufacturer’s product data.

Include leakage, pressure drop, and maximum pressure data.

Indicate materials, construction, and dimensions.

Include damper pressure drop data for all damper sizes in accordance with AMCA 500-D test figure 5.3 (Duct Inlet, Duct Outlet).

Damper to meet or exceed published leakage information when tested in accordance to AMCA 500-D.

Damper to be tested specifically to project specifications in an AMCA approved laboratory when applicable.

Include a copy of the Installation Instructions.

- C.	Product Schedule:  For dampers.  Use same designations indicated on Drawings.

** NOTE TO SPECIFIER **  Delete selection samples if not required.

Samples:  Submit sample of damper to show frame, blades, actuator, accessories, finish, and color.

1.6	INFORMATIONAL SUBMITTALS

** NOTE TO SPECIFIER **  Coordinate "Qualification Data" Paragraph below with qualification requirements in Division 01 Section "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

    - Qualification Data:  For manufacturer and Installer.

Product Test Reports:  For each type of damper, for tests performed by a qualified testing agency.

** NOTE TO SPECIFIER **  Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

Field quality-control reports.

Sample Warranties:  For manufacturer's warranties.

1.7	QUALITY ASSURANCE

    - Manufacturer Qualifications:

The manufacturer shall have implemented the management of quality objectives, continual improvement, and monitoring of customer satisfaction to assure that customer needs and expectations are met.

Manufacturer shall be International Organization for Standardization (ISO) 9001 accredited.

** NOTE TO SPECIFIER **  Insert installer qualifications. Delete if not required.

Installer Qualifications:

USGBC LEED Compliance:  The Work of this section shall be in accordance with applicable portions of the U.S. Green Building Council’s LEED Green Building Rating System. Refer to Divisions 23 and 26 Sections and other related documents bound herein for purposes of complying with this requirement.

  - DELIVERY, STORAGE, AND HANDLING

Delivery:  Deliver materials to site in manufacturer's original, unopened containers and packaging, with labels clearly indicating manufacturer and material.

Storage:  Store materials in a dry area indoors, protected from damage and in accordance with manufacturer's instructions.

Handling:  Handle and lift dampers in accordance with manufacturer's instructions.  Protect materials and finishes during handling and installation to prevent damage.

WARRANTY

Manufacturer shall provide standard limited warranty for damper systems for a period of 5 years (60 months) from date of installation, no more than 60 months after shipment from manufacturing plant. When notified in writing from the Owner of a manufacturing defect, manufacturer shall promptly correct deficiencies without direct financial cost to the Owner.

PART 2	PRODUCTS

2.1	MANUFACTURER

- Ruskin Company, 3900 Dr. Greaves Road, Grandview, Missouri 64030.  Phone (816) 761-7476.  Fax (816) 765-8955.  Web Site http://www.ruskin.com.

- Substitutions:  Not permitted.

- Request for substitutions will be considered in accordance with provisions of Section 01600.

2.2	CONTROL DAMPERS

** NOTE TO SPECIFIER **  Consult Ruskin for assistance in selecting from options for specific applications.

    - Model: CD35 as manufactured by Ruskin Company.

Ratings:

Size: Damper widths from 12 inches (305 mm) to 48 inches (1219 mm) as scheduled or required.

** NOTE TO SPECIFIER **  Performance rating based on 12 inches (305 mm) blade.

Leakage:  Damper shall have a maximum leakage of 17 cfm/sq. ft. (86.3 L/s-m2) @1 inch wg. for a 12 inch (305 mm) damper.

Differential Pressure:  Damper shall have a maximum differential pressure rating of 5 inches w.g. (1.25 kPa) for a 12 inch (305 mm) damper.

Velocity: Damper shall have a maximum velocity rating of 3,000 fpm (914.4 m/min) for a 12 inches (305 mm) blade.

Temperature: Damper shall be rated for -40 degrees F to +240 degrees F (-40 degrees C to +116 degrees C).

Construction:

Frame (when size permits): UniFrame Design Concept (UDC) and shall be roll-formed structural hat channels, reinforced at the corners, formed from a single piece of minimum 16 gauge (1.6mm) galvanized steel.

Blades:

Style:  Single skin, 16 gauge (1.6mm) galvanized steel with three longitudinal grooves for reinforcement.

** NOTE TO SPECIFIER **  Delete action not required.

Action:  Parallel.

Action:  Opposed.

** NOTE TO SPECIFIER **  Delete orientation not required.

Orientation:  Horizontal.

Orientation:  Vertical with thrust washers.

Width:  Nominal 6 inches (152 mm).

Bearings:  Corrosion resistant, molded synthetic sleeve type turning in an extruded hole in the damper frame.

** NOTE TO SPECIFIER **  Extruded bearing hole provides more axle-to-bearing surface.  The bearings will last longer, adding to the life of the damper.

Seals:

** NOTE TO SPECIFIER **  Ruskiprene blade edge seals offer the best leakage performance in the damper industry.  Glue-on or clip-on seals can fall off the damper blade and frame, affecting the leakage rating and damper performance.

Blade:  Blade edge seals shall be polyurethane foam suitable for -40 degrees F to +240 degrees F (-40 degrees C to +116 degrees C) and mechanically locked into the blade edge. Adhesive or clip-on type seals are not acceptable.

Jamb:  Flexible stainless steel metal, compression type to prevent leakage between end of the blade and the damper frame. Blade end overlapping frame or an adhesive type jamb seal is unacceptable.

Linkage:  Concealed out of airstream, within the damper frame to reduce pressure drop and noise. .

** NOTE TO SPECIFIER **  Specify concealed linkage for lower pressure drop and low maintenance.

Axles:  Minimum 1/2 inches (13 mm) diameter plated steel, hexagonal shaped and positively locked into the damper blade (round axles are not acceptable)..

** NOTE TO SPECIFIER **  Delete mounting not required.

Mounting:  Vertical.

Mounting:  Horizontal.

Finish:  Mill galvanized.

** NOTE TO SPECIFIER **  Standard finish is mill galvanized.  Consult Ruskin for assistance in specifying special finishes for specific applications.

- 2.3	ACCESSORIES

Actuator:

** NOTE TO SPECIFIER **  Specify an electric or pneumatic actuator, fail position, and mounting.  Consult Ruskin for assistance in specifying accessories for specific applications. Delete actuator type (electric or pneumatic) not required.

Electric:  120 V, two-position.

Electric:  24 V, two-position.

Electric:  230 V, two-position.

Electric:  24 V, modulating.

** NOTE TO SPECIFIER **  Delete pneumatic type not required.

Pneumatic:  Two-position. 20 to 30 psi (138 to 207 kPa) supply air pressure.

Pneumatic:  Modulating. 20 to 30 psi (138 to 207 kPa) supply air pressure.

** NOTE TO SPECIFIER **  Delete fail position not required.

Fail Position:  Open.

Fail Position:  Closed.

** NOTE TO SPECIFIER **  Delete mounting not required.

Mounting: External side plate.

Mounting: External sleeve.

Mounting: In airstream.

SP 100 Switch Package:

** NOTE TO SPECIFIER **  Switch package indicates actual blade position, not actuator or control shaft position.

Two position indicator switches linked directly to damper blade to remotely indicate damper blade position.

** NOTE TO SPECIFIER **  Delete if not required.

Flange Frame:  1-1/2 inches (38 mm), roll formed as part of frame.

** NOTE TO SPECIFIER **  Delete location not required.

Location: Front.

Location: Rear.

Location: Double.

** NOTE TO SPECIFIER **  T-flange frame is designed for easy installation where T-flange duct connections are used.  T-flange frame provides maximum free area for lowest pressure drop performance, which may be critical in small duct applications.  Delete if not required.

T-Flange Frame:  Minimum 6 inches x 1-3/8 inches x 0.125 inch (152 x 35 x 3.2 mm) aluminum, bolt holes in corners.

Mates To:  TDC, TDF, Ductmate, Nexus, Ward, and other T-flange duct connections.

Performance:  Maximum free area and lowest pressure drop.

Factory Sleeve:  Minimum 20 gage (1.0 mm) thickness, minimum 12 inches (305 mm) length.

** NOTE TO SPECIFIER **  Delete duct transition not required.

Duct Transition Connection:  Round.

Duct Transition Connection:  Oval.

Duct Transition Connection:  Rectangular.

- 2.4	SOURCE QUALITY CONTROL

Factory Tests:  Factory cycle damper and actuator assembly to assure proper operation.

EXECUTION

- 3.1	EXAMINATION

Inspect areas to receive dampers.  Notify the Engineer of conditions that would adversely affect the installation or subsequent utilization of the dampers.  Do not proceed with installation until unsatisfactory conditions are corrected.

- 3.2	INSTALLATION

Install dampers at locations indicated on the drawings and in accordance with manufacturer's installation instructions.

Install dampers square and free from racking with blades orientation as scheduled or required.

Do not compress or stretch damper frame into duct or opening.

Handle damper using sleeve or frame.  Do not lift damper using blades, actuator, or jackshaft.

Install bracing for multiple section assemblies to support assembly weight and to hold against system pressure.  Install bracing as needed.

END OF SECTION