** NOTE TO SPECIFIER **  This document is subject to copyright protection and is property of Ruskin Company.  Ruskin authorizes the Specifier a limited non-exclusive license to use this document (in whole or in part) for the purpose of preparing written product specifications for the CSI MasterFormat category.  Ruskin Company is providing the information contained in this document for informational use, and is provided without representation or warranty of any kind as to the user or any other party, including, without limitation, any implied warranty of merchantability, and fitness for particular purpose, application, or non-infringement. To the greatest extent permitted by applicable law, Ruskin Company assumes no liability, and User assumes all liability and risk, for the use or results from the use of this document or the information contained herein, whether modified by the user or not. Any user of this document should consult www.ruskin.com to verify that the information contained herein is the most current representation of the specified product.

DIVISION 23 HVAC

MODEL CBS8BL BLAST SUPPRESSION DAMPER

Display hidden notes to specifier by using “Tools”/”Options”/“View”/”Hidden Text”.

** NOTE TO SPECIFIER **  This section is based on the products of Ruskin Company, which is located at:

3900 Dr. Greaves Road

Kansas City, Missouri 64030

Tel: (816) 761-7476

Fax: (816) 765-8955

Email: ruskin@ruskin.com

Web: http://www.ruskin.com

Ruskin Manufacturing has been the leading manufacturer of air control solutions for over 50 years. Ruskin has pioneered advanced products for the HVAC Industry and continues to be an industry leader with modern manufacturing equipment, computer-aided design capabilities and an AMCA- registered air performance testing laboratory for research and development. These resources are backed by our experienced engineers and professional staff and reflects Ruskin's commitment to delivering high quality product.

SECTION 23 33 13, Copyright 2016, Ruskin Company.

GENERAL

SECTION INCLUDES

** NOTE TO SPECIFIER **  This section covers Ruskin Company’s heavy duty blast suppression damper model CBS8BL.  Consult Ruskin Company representative for assistance in editing this section for specific applications.

Flanged frame, Heavy duty, galvanized steel blast suppression dampers.

RELATED SECTIONS

** NOTE TO SPECIFIER **  Edit the following list as required for the project.  List other sections with work directly related to the dampers.

Section 23 09 13 – Instrumentation and Control Devices for HVAC; Actuators and Operators; Control Dampers

Section 23 33 00 – Air Duct Accessories

REFERENCES

** NOTE TO SPECIFIER **  Delete references from the list below that are not actually required by the text of the edited section.

AMCA 500 - Test Methods for Louvers, Dampers and Shutters.

AMCA 500-D - Laboratory Methods for Testing Dampers for Ratings.

AMCA 511 – Certified Ratings Program for Air Control Devices.

** NOTE TO SPECIFIER **  Delete if not required.

USGBC: U.S. Green Building Council LEED® Rating System.

DEFINITIONS

** NOTE TO SPECIFIER **  Retain definitions remaining after this Section has been edited.

Damper Terminology:  Definitions of terms for metal louvers contained in AMCA 500 apply to this Section unless otherwise defined in this Section or in referenced standards.

Horizontal Damper:  Damper with horizontal blades; i.e., the axes of the blades are horizontal.

ACTION SUBMITTALS

Comply with requirements of Section 01 33 00 - Submittal Procedures.

Product Data:  Submit manufacturer's product data.

Submit manufacturer's product data, including leakage, pressure drop, and maximum pressure data in accordance with AMCA 500 testing.  Submit data for full range of damper sizes.

Indicate materials, construction, and dimensions.

Include damper pressure drop data for all damper sizes in accordance with AMCA 500-D test figure 5.3 (Ducted Inlet, Ducted Outlet) or figure 5.5 (Bulkhead Mounting).

Damper to be tested specifically to project specifications in an AMCA approved laboratory when applicable.

Include a copy of the Installation Instructions.

Shop Drawings:

Submit shop drawings indicating materials, construction, dimensions, accessories, and installation details.

Product Schedule:  For dampers.  Use same designations indicated on Drawings.

** NOTE TO SPECIFIER **  Delete selection samples if not required.

Samples:  Submit sample of damper to show frame, blades, actuator, accessories, finish, and color.

INFORMATIONAL SUBMITTALS

** NOTE TO SPECIFIER **  Coordinate "Qualification Data" Paragraph below with qualification requirements in Division 01 Section "Quality Requirements" (01 40 00) and as may be supplemented in "Quality Assurance" Article.

Qualification Data:  For manufacturer and Installer.

Product Test Reports:  For each type of damper, for tests performed by a qualified testing agency.

** NOTE TO SPECIFIER **  Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

Field quality-control reports.

Sample Warranties:  For manufacturer's warranties.

QUALITY ASSURANCE

Manufacturer Qualifications:

The manufacturer shall have implemented the management of quality objectives, continual improvement, and monitoring of customer satisfaction to assure that customer needs and expectations are met.

Manufacturer shall be International Organization for Standardization (ISO) 9001 accredited.

Dampers shall be manufactured by a reputable company who is a member of the Air Movement Control Association (AMCA).

DELIVERY, STORAGE, AND HANDLING

Delivery:  Deliver materials to site in manufacturer's original, unopened containers and packaging, with labels clearly indicating manufacturer and material.

Storage:  Store materials in a dry area indoors, protected from damage and in accordance with manufacturer's instructions.

Handling:  Handle and lift dampers in accordance with manufacturer's instructions.  Protect materials and finishes during handling and installation to prevent damage.

PROJECT CONDITIONS

Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results.  Do not install products under environmental conditions outside manufacturer's absolute limits.

WARRANTY

Manufacturer shall provide standard limited warranty for damper systems for a period of five years (60 months) from date of installation, no more than 60 months after shipment from manufacturing plant. When notified in writing from the Owner of a manufacturing defect, manufacturer shall promptly correct deficiencies without direct financial cost to the Owner.

PRODUCTS

MANUFACTURERS

Ruskin Company, 3900 Dr. Greaves Road, Kansas City, Missouri 64030.  Phone (816) 761-7476.  Fax (816) 765-8955.  Web Site http://www.ruskin.com.

** NOTE TO SPECIFIER **  Delete one of the following two paragraphs; coordinate with requirements of Division 1 section on product options and substitutions.

Substitutions:  Not permitted.

Requests for substitutions will be considered in accordance with provisions of Section 01 60 00.

** NOTE TO SPECIFIER **  Ruskin model CBS8BL is specifically designed to provide a level of  protection against blast events and instantaneous pressure changes. Applications include prevention of dust/vapor cloud explosions from storage areas containing volatile materials, building de-pressurization from tornado activity, or system protection. CBS8BL is to be flange mounted and can be constructed from various materials.

BACKDRAFT DAMPERS

** NOTE TO SPECIFIER **   Both direction of Normal Airflow and direction of Blast must be specified:  Either Blast and Normal Airflow are in same direction, or Blast and Normal Airflow are opposite direction of each other.

Model:  CBS8BL as manufactured by Ruskin Company.

Size: As indicated on drawings.

Construction:

Frame: Damper frame shall be one piece construction. 12 inches (305 mm) deep by 2 inches (52 mm) flanged by 10 ga. (2 mm) thick. Sleeve or channel with inner frame is not acceptable. Refer to drawings for square to round transitions required.

Blades: The damper blades shall be airfoil shaped double skin. Minimum 14 ga. (2 mm) skin. Blade orientation is horizontal (standard).

** NOTE TO SPECIFIER **  Delete blade edge seal not required.

Blade Edge Seals:  None (standard).

Blade Edge Seals:  EPDM (maximum 250 degree F, 121 degree C).

Blade Edge Seals:  Silicone (maximum 400 degree F, 204 degree C).

** NOTE TO SPECIFIER **  Delete jamb seal not required.

Blade Jamb Seals:  None (standard).

Blade Jamb Seals:  Neoprene (maximum 250 degree F, 121 degree C).

Bearings: 2-bolt, flange, relubricable ball bearings bolted to the frame (Standard).

Linkage: Damper blade linkage shall be minimum 3/16 inch thick by 3/4 inch (5 mm by 19 mm) bar located on side of damper out of air stream. Pivot pins in linkage shall be stainless steel. Bronze pins or bushings are not acceptable. Linkage shall include externally mounted release springs and adjustable tension to keep damper open until blast of specified pressure force blades closed.

Axles: Minimum 3/4 inch (19 mm) diameter plated steel, full length.

** NOTE TO SPECIFIER **  Delete material not required.

Material of Construction:  Galvanized steel mill finish (standard).

Material of Construction:  Type 304 stainless steel mill finish.

Material of Construction:  Type 316 stainless steel mill finish.

** NOTE TO SPECIFIER **  Delete mounting hole pattern not required.

Mounting Holes: None (standard).

Mounting Holes: Both flanges.

Mounting Holes: As detailed or required.

Performance Data:

** NOTE TO SPECIFIER **  Dampers may tolerate higher temperatures, pressures, and velocities than those specified.  Consult Ruskin when a damper is to be applied in conditions exceeding recommended maximums.

Assembly:  Factory assembled and tested damper components.

Damper shall be designed to withstand blast pressure of up to 44 psi (303 kPa).

Maximum System Velocity:  4,000 feet per minute (1219 m/min).

** NOTE TO SPECIFIER **  Delete if not required.

ACCESSORIES

** NOTE TO SPECIFIER **  Delete option not required.

Automatic Blade Lock: Linkage mechanism designed to lock (secure) the blades in the closed position after the blast event subsides; linkage mechanism readily allows blades to be reset to the open position afterwards.  (Standard).

Automatic Blade Lock: None.

** NOTE TO SPECIFIER **  Delete duct transition not required.

Damper Transition Connection:  Round.  Indicate one or both sides of damper.

Duct Transition Connection:  Oval.  Indicate one or both sides of damper.

SOURCE QUALITY CONTROL

Factory Tests:  Factory cycle damper assembly to assure proper operation.

EXECUTION

EXAMINATION

Inspect areas to receive dampers.  Notify the Architect of conditions that would adversely affect the installation or subsequent utilization of the dampers.  Do not proceed with installation until unsatisfactory conditions are corrected.

If opening preparation is the responsibility of another installer, notify Architect of unsatisfactory preparation before proceeding.

INSTALLATION

Install dampers at locations indicated on the drawings and in accordance with manufacturer's installation instructions.

Install dampers square and free from racking with blades orientation as scheduled or required.

Do not compress or stretch damper frame into duct or opening.

Handle damper using frame or lifting lugs (if provided).  Do not lift damper using blades or linkage.

Install bracing for multiple section assemblies to support assembly weight and to hold against system pressure.  Install bracing as needed.

END OF SECTION